{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["Sheet2","Ark1","Kuldeanlegg","Sheet1","Sheet3","Sheet4"],"not_rendered":{"charts":2,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet2","index":0,"n_rows":31,"n_cols":4,"rows_kept":31,"cut":false,"hidden":false,"merged":[]}
[null,"Tørkeanlegg:"]
[null,"Lufttrykk","Pa",101350]
[null,"Luftmengde","m3/h",20720]
[null,null,"m3/s",{"$f":"D3/3600","v":5.7555555555555555}]
["Inngående luftmengde"]
[null,"Temperatur","oC",22]
[null,"Relativ fuktighet","%",50]
[null,"Tetthet","kg/m3",{"$f":"1/HX_Vtoerr_trh(D2,D6,D7)","v":1.1421046482250137}]
[null,"Entalpi","J/kg",{"$f":"HX_H_trh(D2,D6,D7)","v":44615.186391650474}]
[null,"Absolutt fuktighet","kg/kg",{"$f":"HX_X_trh(D2,D6,D7)","v":8.4983007998471576E-3}]
[null,"Temperatur ut ","oC",13.3]
[null,"Duggpunkt","oC",{"$f":"HX_Tdugg_trh(D2,D6,D7)","v":11.109274086579029}]
["Varmeveksler"]
["Effektivitet",null,"%",0.75]
["Kjøling ned til duggpunkt"]
[null,"Entalpi","J/kg",{"$f":"HX_H_trh(D2,D12,D17)","v":33052.794673183227}]
[null,"Relativ fuktighet","%",100]
[null,"Ytelse","W",{"$f":"D4*D8*(D9-D16)","v":76004.766300028889}]
[]
[]
[]
[]
["Fordamper"]
[null,"Fordampningstemperature","oC",0]
[null,"Overflatetemperatur","oC",{"$f":"D24+2","v":2}]
[null,"Ralativ fuktighet","%",100]
[null,"Entalpi ved overflate","J/kg",{"$f":"HX_H_trh(D2,D25,D26)","v":13387.181959050151}]
[null,"Absolutt fuktighet","kg/kg",{"$f":"HX_X_trh(D2,D25,D26)","v":4.5091484334993997E-3}]
[null,"Ytelse","W",{"$f":"D4*D8*(D16-D27)","v":129270.85804378038}]
[null,"Utfelt fuktighet","kg/s",{"$f":"D4*D8*(D10-D28)","v":2.6222480670258865E-2}]
[null,null,"kg/h",{"$f":"D30*3600","v":94.400930412931913}]

{"sheet":"Ark1","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Kuldeanlegg","index":2,"n_rows":35,"n_cols":15,"rows_kept":35,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Kuldemedium",null,"R717",null,"R404a","R404a","R404a","R404a"]
[]
[null,"Kondenseringstemperatur","oC",40,null,30,25,20,15]
[null,"Kondenseringstrykk","Pa",{"$f":"R_PsatgasT(D2,D4)","v":1554576.691354516},null,{"$f":"R_PsatgasT(F2,F4)","v":1416011.893891769},{"$f":"R_PsatgasT(G2,G4)","v":1243026.457186914},{"$f":"R_PsatgasT(H2,H4)","v":1086414.120225135},{"$f":"R_PsatgasT(I2,I4)","v":945094.74527835893}]
[null,"Fordampningstemperatur","oC",-10,null,-10,-10,-10,-10]
[null,"Fordampningstrykk","Pa",{"$f":"R_PsatgasT(D2,D6)","v":290768.39865545143},null,{"$f":"R_PsatgasT(F2,F6)","v":433298.62325353548},{"$f":"R_PsatgasT(G2,G6)","v":433298.62325353548},{"$f":"R_PsatgasT(H2,H6)","v":433298.62325353548},{"$f":"R_PsatgasT(I2,I6)","v":433298.62325353548}]
[null,"Trykkforhold","-",{"$f":"D5/D7","v":5.346443074773835},null,{"$f":"F5/F7","v":3.2679815210564835},{"$f":"G5/G7","v":2.8687523811022673},{"$f":"H5/H7","v":2.5073103442321414},{"$f":"I5/I7","v":2.1811625852440266}]
[null,"Volumetrisk virkningsgrad","-",0.7,null,0.7,0.7,0.7,0.7]
[null,"Isentropisk virkningsgrad","-",0.7,null,0.7,0.7,0.7,0.7]
["Punkt"]
[1,"Overhetning","oC",5,null,5,5,5,5]
[null,"Spesifikk entalpi","J/kg",{"$f":"R_HgasTP(D2,(D6+D12),D7)","v":1624603.9514386449},null,{"$f":"R_HgasTP(F2,(F6+F12),F7)","v":366692.33231503889},{"$f":"R_HgasTP(G2,(G6+G12),G7)","v":366692.33231503889},{"$f":"R_HgasTP(H2,(H6+H12),H7)","v":366692.33231503889},{"$f":"R_HgasTP(I2,(I6+I12),I7)","v":366692.33231503889}]
[null,"Spesifikk entropi","J/kgK",{"$f":"R_SgasTP(D2,(D6+D12),D7)","v":6365.3964982328062},null,{"$f":"R_SgasTP(F2,(F6+F12),F7)","v":1635.6977327321499},{"$f":"R_SgasTP(G2,(G6+G12),G7)","v":1635.6977327321499},{"$f":"R_SgasTP(H2,(H6+H12),H7)","v":1635.6977327321499},{"$f":"R_SgasTP(I2,(I6+I12),I7)","v":1635.6977327321499}]
[null,"Spesifikk volum","m3/kg",{"$f":"R_VgasTP(D2,(D6+D12),D7)","v":0.42823455727508941},null,{"$f":"R_VgasTP(F2,(F6+F12),F7)","v":4.7372250676846153E-2},{"$f":"R_VgasTP(G2,(G6+G12),G7)","v":4.7372250676846153E-2},{"$f":"R_VgasTP(H2,(H6+H12),H7)","v":4.7372250676846153E-2},{"$f":"R_VgasTP(I2,(I6+I12),I7)","v":4.7372250676846153E-2}]
["2s","Spesifikk entalpi","J/kg",{"$f":"R_HgasSP(D2,D17,D5)","v":1877929.7702137991},null,{"$f":"R_HgasSP(F2,F17,F5)","v":391162.3469547655},{"$f":"R_HgasSP(G2,G17,G5)","v":388499.54662623833},{"$f":"R_HgasSP(H2,H17,H5)","v":385727.61206665513},{"$f":"R_HgasSP(I2,I17,I5)","v":382844.42596136231}]
[null,"Spesifikk entropi","J/kgK",{"$f":"D14","v":6365.3964982328062},null,{"$f":"F14","v":1635.6977327321499},{"$f":"G14","v":1635.6977327321499},{"$f":"H14","v":1635.6977327321499},{"$f":"I14","v":1635.6977327321499},null,null,null,"p","h","t"]
[null,"Temperatur","oC",{"$f":"R_TgasHP(D2,D16,D5)","v":119.4363420273519}," ",{"$f":"R_TgasHP(F2,F16,F5)","v":38.503968381742773},{"$f":"R_TgasHP(G2,G16,G5)","v":33.039588647253538},{"$f":"R_TgasHP(H2,H16,H5)","v":27.617944706652171},{"$f":"R_TgasHP(I2,I16,I5)","v":22.22170698438595},null,null,1,{"$f":"D7","v":290768.39865545143},{"$f":"D13","v":1624603.9514386449},{"$f":"D6+D12","v":-5}]
[2,"Spesifikk entalpi","J/kg",{"$f":"D13+(D16-D13)/D10","v":1986497.9782602938},null,{"$f":"F13+(F16-F13)/F10","v":401649.49608607689},{"$f":"G13+(G16-G13)/G10","v":397845.49561675236},{"$f":"H13+(H16-H13)/H10","v":393885.58910306211},{"$f":"I13+(I16-I13)/I10","v":389766.75180978666},null,null,2,{"$f":"D5","v":1554576.691354516},{"$f":"D19","v":1986497.9782602938},{"$f":"D20","v":162.03414428075931}]
[null,"Temperatur","oC",{"$f":"R_TgasHP(D2,D19,D5)","v":162.03414428075931},null,{"$f":"R_TgasHP(F2,F19,F5)","v":48.439448977389077},{"$f":"R_TgasHP(G2,G19,G5)","v":42.171678284639938},{"$f":"R_TgasHP(H2,H19,H5)","v":35.822330106627533},{"$f":"R_TgasHP(I2,I19,I5)","v":29.374641744202791},null,null,3,{"$f":"M19","v":1554576.691354516},{"$f":"D22","v":537639.89202611591},{"$f":"D4-D21","v":37}]
[3,"Underkjøling i kondensator","oC",3,null,3,3,3,3,null,null,4,{"$f":"M18","v":290768.39865545143},{"$f":"N20","v":537639.89202611591},{"$f":"D6","v":-10}]
[null,"Spesifikk entalpi","J/kg",{"$f":"R_HsatliqT(D2,(D4-D21))","v":537639.89202611591},null,{"$f":"R_HsatliqT(F2,(F4-F21))","v":241022.12705588099},{"$f":"R_HsatliqT(G2,(G4-G21))","v":232904.31888057059},{"$f":"R_HsatliqT(H2,(H4-H21))","v":225040.6447706357},{"$f":"R_HsatliqT(I2,(I4-I21))","v":217402.25254119941},null,null,1,{"$f":"M18","v":290768.39865545143},{"$f":"N18","v":1624603.9514386449},{"$f":"O18","v":-5}]
[4,"Spesifikk entalpi","J/kg",{"$f":"D22","v":537639.89202611591},null,{"$f":"F22","v":241022.12705588099},{"$f":"G22","v":232904.31888057059},{"$f":"H22","v":225040.6447706357},{"$f":"I22","v":217402.25254119941}]
[]
[null,"Spesifikk kuldeytelse","J/kg",{"$f":"(D13-D23)","v":1086964.059412529},null,{"$f":"(F13-F23)","v":125670.2052591579},{"$f":"(G13-G23)","v":133788.0134344683},{"$f":"(H13-H23)","v":141651.68754440319},{"$f":"(I13-I23)","v":149290.07977383948},null,null,null,null,"R717"]
[null,"Spesifikt kraftforbruk","J/kg",{"$f":"(D19-D13)","v":361894.02682164893},null,{"$f":"(F19-F13)","v":34957.163771038002},{"$f":"(G19-G13)","v":31153.163301713474},{"$f":"(H19-H13)","v":27193.256788023224},{"$f":"(I19-I13)","v":23074.419494747766},null,null,null,null,0]
[null,"Spesifik kondensatorytelse","J/kg",{"$f":"(D19-D22)","v":1448858.0862341779},null,{"$f":"(F19-F22)","v":160627.3690301959},{"$f":"(G19-G22)","v":164941.17673618178},{"$f":"(H19-H22)","v":168844.94433242641},{"$f":"(I19-I22)","v":172364.49926858724}]
[null,"COP","-",{"$f":"D25/D26","v":3.0035424153276065},null,{"$f":"F25/F26","v":3.5949771578229588},{"$f":"G25/G26","v":4.294524191291667},{"$f":"H25/H26","v":5.2090740233362229},{"$f":"I25/I26","v":6.4699387045390724},null,null,null,null,{"$f":"R_PsatgasT(N25,N26)","v":429351.64557056891}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"R_CPliqTP(\"R717\",-20,1000000)","v":4541.302791554358}]
[null,"Slagvolum","m3/h",250,null,250,250,250,250]
[null,"Massestrøm","kg/s",{"$f":"(D30/3600)*D9/D15","v":0.11351515258467171},null,{"$f":"(F30/3600)*F9/F15","v":1.0261516059837636},{"$f":"(G30/3600)*G9/G15","v":1.0261516059837636},{"$f":"(H30/3600)*H9/H15","v":1.0261516059837636},{"$f":"(I30/3600)*I9/I15","v":1.0261516059837636}]
[]
[null,"Kuldeytelse","kW",{"$f":"D31*D25/1000","v":123.38689105826739},null,{"$f":"F31*F25/1000","v":128.95668295099409},{"$f":"G31*G25/1000","v":137.28678484715698},{"$f":"H31*H25/1000","v":145.35610666399961},{"$f":"I31*I25/1000","v":153.19425511736958},null,null,null,null,"="]
[null,"Kfraftforbruk","kW",{"$f":"D31*D26/1000","v":41.080455674140758},null,{"$f":"F31*F26/1000","v":35.871349744288082},{"$f":"G31*G26/1000","v":31.96786855352773},{"$f":"H31*H26/1000","v":27.904404124958912},{"$f":"I31*I26/1000","v":23.677852621678486}]
[null,"Kondensatorytelse","kW",{"$f":"D31*D27/1000","v":164.46734673240815},null,{"$f":"F31*F27/1000","v":164.82803269528219},{"$f":"G31*G27/1000","v":169.25465340068473},{"$f":"H31*H27/1000","v":173.26051078895856},{"$f":"I31*I27/1000","v":176.87210773904806}]

{"sheet":"Sheet1","index":3,"n_rows":25,"n_cols":7,"rows_kept":25,"cut":false,"hidden":false,"merged":[]}
[]
[null,null,null,"R717","R717","R717","R717"]
[null,null,null,null,null,"kokepunkt"]
[null,"Kritisk punkt",null,{"$f":"R_Tcrit(D2)","v":132.25299999999999}]
[null,null,null,{"$f":"D4-0.1","v":132.15299999999999},{"$f":"R_PsatliqT($E$2,D5)","v":11313569.44554266},{"$f":"R_HsatliqT($F$2,D5)","v":1251425.508804444},{"$f":"R_HsatgasT($G$2,D5)","v":1308757.437513134}]
[null,null,null,{"$f":"D5-0.5","v":131.65299999999999},{"$f":"R_PsatliqT($E$2,D6)","v":11214226.610937109},1211345.3526697969,{"$f":"R_HsatgasT($G$2,D6)","v":1346569.890556966}]
[null,null,null,{"$f":"D6-1","v":130.65299999999999},11017598.820843469,1174437.7273726689,{"$f":"R_HsatgasT($G$2,D7)","v":1382903.3301024479}]
[null,null,null,{"$f":"D4-2","v":130.25299999999999},10939826.66350292,1164169.9741961539,1393239.9874510481]
[null,null,null,{"$f":"D8-4","v":126.25299999999999},10189613.786581131,1098198.152612237,1457644.492401564]
[null,null,null,{"$f":"D9-10","v":116.25299999999999},8506553.881857764,999833.81616879883,1535647.562108773]
[null,null,null,{"$f":"D10-10","v":106.25299999999999},7056500.7158669997,924698.91873001994,1579242.6794872319]
[null,null,null,96.252999999999986,5806170.1136946296,858767.93621614436,1607772.4244003161]
[null,null,null,86.252999999999986,4731759.1647108467,798151.86524188949,1627130.172740767]
[null,null,null,76.252999999999986,3814027.5896762321,741112.54371188872,1640057.8273044601]
[null,null,null,66.252999999999986,3036350.444535716,686691.32387436519,1648084.487427118]
[null,null,null,56.252999999999986,2383750.0484471931,634287.26793534891,1652154.6378004551]
[null,null,null,46.252999999999986,1842382.0796737019,583486.45454071194,1652896.4798976639]
[null,null,null,36.252999999999986,1399245.1466157001,533980.89161804051,1650754.0207935511]
[null,null,null,26.252999999999986,1042018.014086533,485526.76871571952,1646067.9142785219]
[null,null,null,16.252999999999986,759020.78540294385,437923.58635251317,1639123.107394133]
[null,null,null,6.2529999999999859,539248.6599021469,391006.71261038608,1630166.6843052499]
[null,null,null,-3.7470000000000141,372426.76694741403,344649.78931603458,1619417.837055675]
[null,null,null,{"$f":"D22-10","v":-13.747000000000014},249073.43360461949,298773.49113806232,1607070.160728022]
[null,null,null,-23.747000000000014,160569.04851923769,253352.92119364711,1593315.758143892]
[null,null,null,-33.747000000000014,99249.535359061774,208404.10081988861,1578435.8746016959]

{"sheet":"Sheet3","index":4,"n_rows":17,"n_cols":9,"rows_kept":17,"cut":false,"hidden":false,"merged":[]}
["EXAMPLE"]
[]
["Mollier diagram",null,null,null,null,null,null,null,"R717"]
[null,null,null,null,null,"Condenser temp",null,null,30]
["Temperature",20,null,null,null,"Evapratpor temperatur",null,null,-10]
["Reletive humidity",50,null,null,null,"Cond pressur",null,null,{"$f":"R_PsatgasT(I3,I4)","v":1166562.2091717061}]
["Absolute humidity",{"$f":"HX_X_trh(101350,B5,B6)","v":7.5038370581822613E-3},null,null,null,"Evap pressure",null,null,{"$f":"R_PsatgasT(I3,I5)","v":290768.39865545143}]
["Dew point",{"$f":"HX_Tdugg_trh(101350,B5,B6)","v":9.2717778324567686},null,null,null,"Pressure ratio",null,null,{"$f":"I6/I7","v":4.0119979150624081}]
["Enthalpy",{"$f":"HX_H_trh(101350,B5,B6)","v":39967.77550512951}]
["Wet buld tem",{"$f":"HX_T_hrh(101350,B9,100)","v":13.741880230049739},null,null,1,"Enthaplpy",null,null,{"$f":"R_HsatgasT(I3,I5)","v":1611873.426123911}]
[null,null,null,null,null,"Entropy",null,null,{"$f":"R_SsatgasT(I3,I5)","v":6317.4780322086744}]
[]
[null,null,null,null,"2s","Enthalpy",null,null,{"$f":"R_HgasSP(I3,I11,I6)","v":1810197.919280753}]
[null,null,null,null,null,"Isentropi eff",null,null,0.7]
[null,null,null,null,2,"Enthalpy",null,null,{"$f":"I10+(I13-I10)/I14","v":1895194.1306336853}]
[null,null,null,null,null,"Temperature",null,null,{"$f":"R_TgasHP(I3,I15,I6)","v":122.0452731455874}]
[null,null,null,null,null,null,null,null,{"$f":"R_HsatliqT(I3,0)","v":361960.31047730462}]

{"sheet":"Sheet4","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}